## EXCEL-S WindCAD
WindCad Turbine Performance Model
BWC EXCEL-S, Grid - Intertie |  |  |  | Tier/neo-SH3055-23-BWC
Prepared For: | SWCC
Site Location: | Reference
Data Source: | AWEA Standard
Date: | 2026-07-30 05:35
Inputs: |  | Results:
Ave. Wind (m/s) = | 5 |  | Hub Average Wind Speed (m/s) = | 5
Weibull K = | 2 |  | Air Density Factor = | -0%
Site Altitude (m) = | 0 |  | Average Output Power (kW) = | 1.5099
Wind Shear Exp. = | 0.2 |  | Daily Energy Output (kWh) = | 36.2374
Anem. Height (m) = | 30 |  | Annual Energy Output (kWh) = | 13226.6505
Tower Height (m) = | 30 |  | Monthly Energy Output = | 1102.2209
Turbulence Factor = | 0% |  | Percent Operating Time = | 67.87%
Weibull Performance Calculations
Wind Speed Bin (m/s) | Power (kW) | Wind Probability (f) | Net kW @ V
1 | 0 | 6.139% | 0
2 | 0 | 11.17% | 0
3 | 0.14 | 14.29% | 0.020011
4 | 0.43 | 15.27% | 0.06565
5 | 0.88 | 14.35% | 0.12628
6 | 1.51 | 12.15% | 0.1835
7 | 2.35 | 9.391% | 0.22069
8 | 3.43 | 6.673% | 0.22888
9 | 4.8 | 4.381% | 0.21027
10 | 6.42 | 2.666% | 0.17115
11 | 8.21 | 1.508% | 0.12377
12 | 10.02 | 0.7936% | 0.079516
13 | 11.37 | 0.3894% | 0.044269
14 | 11.76 | 0.1782% | 0.020961
15 | 12.06 | 0.07619% | 0.009189
16 | 12.14 | 0.03044% | 0.0036949
17 | 12.15 | 0.01137% | 0.001381
18 | 12.1 | 0.00397% | 0.00048043
19 | 11.92 | 0.001298% | 0.00015469
20 | 11.44 | 0.000397% | 4.542e-05
2008, BWC | Totals: | 99.47% | 1.5099
Weibull Calculations:
Wind speed probability is calculated as a Weibull curve defined by the average wind speed and a shape factor, K. To facilitate piece-wise integration, the wind speed range is broken down into "bins" of 1 m/s in width (Column 1). For each wind speed bin, instantaneous wind turbine power (W, Column 2)) is multiplied by the Weibull wind speed probability (f, Column 3). This cross product (Net W, Column 4) is the contribution to average turbine power output contributed by wind speeds in that bin. The sum of these contributions is the average power output of the turbine on a continuous, 24 hour, basis.
Best results are achieved using annual or monthly average wind speeds. Use of daily or hourly average speeds is not recommended.
Instructions:
Inputs: Use annual or monthly Average Wind speeds. If Weibull K is not known, use K = 2 for inland sites, use 3 for coastal sites, and use 4 for island sites and trade wind regimes. Site Altitude is meters above sea level. Wind Shear Exponent is best assumed as 0.18. For rough terrain or high turbulence use 0.22. For very smooth terrain or open water use 0.11. Anemometer Height is for the data used for the Average Wind speed. If unknown, use 10 meters. Tower Height is the nominal height of the tower, eg.: 24 meters. Turbulence Factor is a derating for turbulence, site variability, and other performance influencing factors -- typical turbulence has already been incorporated into the model. Use 0.00 (0%) for level sites with limited obstructions. Use -0.10 ( negative 10%) for flat, clear sites on open water. Use 0.05 to 0.15 (5% to 15%) for rolling hills or mountainous terrain.
Results: Hub Average Wind Speed is corrected for wind shear and used to calculate the Weibull wind speed probability. Air Density Factor is the reduction from sea level performance. Average Power Output is the average continuous equivalent output of the turbine. Daily Energy Output is the average energy produced per day. Annual and Monthly Energy Outputs are calculated using the Daily value. Percent Operating Time is the time the turbine should be producing some power.
Limitations: This model uses a mathmatical idealization of the wind speed probability. The validity of this assumption is reduced as the time period under consideration (ie, the wind speed averaging period) is reduced. This model is best used with annual or monthly average wind speeds. Use of this model with daily or hourly average wind speed data is not recommended because the wind will not follow a Weibull distribution over short periods. The data used in creating the power curve was generated at the BWC test site in Norman, OK. Consult Bergey Windpower Co. for special needs. Your performance may vary.
10 kW

## Power curve data
Wind Speed Bin (m/s) | Power (kW) at sea level
1 | 0
2 | 0
3 | 0.14
4 | 0.43
5 | 0.88
6 | 1.51
7 | 2.35
8 | 3.43
9 | 4.8
10 | 6.42
11 | 8.21
12 | 10.02
13 | 11.37
14 | 11.76
15 | 12.06
16 | 12.14
17 | 12.15
18 | 12.1
19 | 11.92
20 | 11.44